## Summary
ITEM NO | DESCRIPTION OF THE ITEM | LIST | PRICE
1 | Preliminary and General | List A
VAALDAM SUBSTATION EXTENSION
2 | Site Works | List B
3 | Earth Grid | List C
4 | Substation Fencing | List D
5 | Civil Work | List E
6 | Buildings | List F
7 | Steel Work | List G
8 | Equipment | List H
9 | Control Plant | List I
10 | Training & Spares | List J
THEMBA KHUBEKA ELECTRIFICATION
11 | Themba Khubeka Reticulation - MV Network | List K
12 | Themba Khubeka Reticulation - LV Network | List L
13 | Themba Khubeka Reticulation - House Connections | List M
14 | Themba Khubeka Reticulation - Switchgear | List N
88 KV LINE REPAIRS, 88 / 11 KV SUBSTATION REPAIRS & OTHER
15 | Substation Repair & Commissioning | List O
16 | Overhead Line Repair | List P
17 | SUBTOTAL A - LIST A to O |  | 0
18 | Plus: 10 % Contingencies |  | 0
19 | Plus: 5 % Escalation |  | 0
20 | SUBTOTAL B |  | 0
21 | Plus: 15 % VAT |  | 0
22 | TOTAL TENDER PRICES - SUBTOTAL B & VAT (Carried forward to Section 3, Part C1.1, Page 1 of tender document) |  | 0
| TENDERER'S SIGNATURE: | _________________________________________
| COMPANY NAME: | _________________________________________
| ADDRESS: | _________________________________________
NOTE: - TENDERERS ARE RESPONSIBLE TO INSERT ALL EXCEL FORMULAS AND CHECK FOR ARITHMETIC ERRORS
NOTE: - THE TENDERER SHALL POPULATE THE BILL OF QUANTITIES BY HAND IN THE BID SUBMISSION DOCUMENT
NOTE: - THE TENDERER SHALL EMAIL THE POPULATED BOQ IN PDF AND RAW EXCEL FORMAT TO LYON@LYON.CO.ZA
NOTE: - AT THE TENDER CLOSING TIME (FOR EVALUATION PURPOSES)
LV AUXILIARY SUPPLY (Sicelo Substation)
The supply at Sicelo Substation will come from the Midvaal Switchgear Room

## LIST A - P & G
ITEM | DESCRIPTION | UNIT | QTY | UNIT RATE | TOTAL
1. | PRELIMINARIES
Amount allowed for all expenses, regarding the following:
1.1 | CONTRACTUAL REQUIREMENTS - FIXED AMOUNT
1.1.1 | Nett price for the fulfilment of the Tender Requirements, Conditions of Contract and Performance
Security/Security Bond. Performance Security to remain valid until date of issue of the Final Completion
| Certificate or within 28 days after expiry Defects Notification Period | Sum | 1 |  | 0
0
1.1.2 | Insurance of the Works in the joint names of the Employer and Contractor, Insurance of the Construction |  |  |  | 0
| Plant to its full replacement value and Third Party Insurance | Sum | 1 |  | 0
0
1.1.3 | Site establishment, which includes, site office, site store, laydown area, temporary housing, security fence, |  |  |  | 0
| sanitary, toilets, obtaining water, electrical connection, etc. | Sum | 1 |  | 0
0
1.1.4 | Pegging and surveying of the route by a qualified surveyor: MV route including all pole positions, |  |  |  | 0
| anchors, stand boundaries for cable positions, etc. | Sum | 1 |  | 0
1.1.5 | Surveying of the as-built route by a qualified surveyor: MV route including all pole positions, |  |  |  | 0
| anchors, stand boundaries for cable positions, etc. | Sum | 1 |  | 0
0
1.1.6 | Pegging and surveying of the route by a qualified surveyor: LV route including all terminal pole and bend |  |  |  | 0
| points, etc. | Sum | 1 |  | 0
0
1.1.7 | Pegging and surveying of the substation terrace by a qualified surveyor: Substation levels, fence position, |  |  |  | 0
| equipment positions and reference pegs | Sum | 1 |  | 0
0
1.1.8 | Reinstating of missing S.G. pegs prior to construction of any works and obtaining Surveyors Certificate of |  |  |  | 0
| Compliance (Pr. Land Surveyor) | Sum | 1 |  | 0
0
1.1.9 | Determining and locating of existing services as well as management of wayleaves througout the delivery of |  |  |  | 0
| the works, | Sum | 1 |  | 0
0
1.1.10 | Erecting of temporary obstructions and barricades | Sum | 1 |  | 0
0
1.1.11 | CONSTRUCTION NOTICE BOARD ( mm. 2600 X 1600) | Each | 2 |  | 0
0
1.1.12 | Cleaning of the site, removal of all refuse, rubble, rock, etc. prior to handing over of every phase | Sum | 1 |  | 0
0
1.1.13 | Obtaining permits, arranging for outages and switching with relevant Authorities | Sum | 1 |  | 0
0
1.1.14 | Obtaining access to the Eskom Website (scot.eskom.co.za) for access to the relevant Eskom Standards, |  |  |  | 0
| and obtaining Eskom FSOU authorisation before executing the Works | Sum | 1 |  | 0
0
1.1.15 | Tools, material, safety clothing, and the appropriate PPE for the labourers (incl. local labourers) to conduct |  |  |  | 0
| their work in accordance with safety requirements | Sum | 1 |  | 0
0
1.1.16 | Medical evaluation and induction cost for all staff | Sum | 1 |  | 0
0
1.1.17 | As built drawings and manuals (5 x sets). As builts to include surveying of the works by a qualified |  |  |  | 0
| surveyor, i.e. MV and LV conductors, equipment positions and any relevant site information (drawings to be |  |  |  | 0
| issued in CAD format) | Sum | 1 |  | 0
0
1.1.18 | Removal from site following completion of the Works | Sum | 1 |  | 0
0
1.1.19 | Temporary removal from site for an undetermined period following completion of a section of the work and |  |  |  | 0
| re-establishment to complete the remainder of the Works | Sum | 0 |  | 0
0
1.2 | COMPLY WITH THE FOLLOWING SAFETY, HEALTH, ENVIRONMENTAL AND |  |  |  | 0
| QUALITY (SHEQ) REQUIREMENTS - FIXED AMOUNT |  |  |  | 0
1.2.1 | Adherence to Construction Regulations of the OHS Act | Sum | 1 |  | 0
0
1.2.2 | Compile a Health and Safety Plan (H & S Plan) | Sum | 1 |  | 0
0
1.2.3 | Compile a Risk Assessment for activities (RA) | Sum | 1 |  | 0
0
1.2.4 | Comply with Environmental Management Plan (EMP) | Sum | 1 |  | 0
0
1.2.5 | Submit proof of calibration of equipment, eg. Crimper, HV test apparatus, breaking failure test of |  |  |  | 0
| terminations and joints of ACSR OH Lines etc. | Sum | 1 |  | 0
0
1.2.6 | Compile a SHEQ File to also include all the above distinct sections | Sum | 1 |  | 0
0
1.2.7 | Construction work notification and permit application (assist the Employer to obtain a construction permit) | Sum | 1 |  | 0
0
1.3 | TOTAL TIME RELATED COST BASED ON MONTHLY EXPENDITURE - ADJUSTABLE |  |  |  | 0
| WITH CONTRACT PERIOD | Sum | 1 |  | 0
| The running cost of the project related to the contract period, which will also be used to adjust the cost if an |  |  |  | 0
| event occurs that becomes the Employers Risk |  |  |  | 0
1.3.1 | Head office overhead cost and contractual obligations | Sum | 1 |  | 0
0
1.3.2 | Site overhead cost | Sum | 1 |  | 0
0
1.3.3 | Material-store cost on site | Sum | 1 |  | 0
0
1.3.4 | Material-store cost off site | Sum | 1 |  | 0
0
1.3.5 | Maintenance of setting out of the works by a qualified surveyor | Sum | 1 |  | 0
0
1.3.6 | Contracts Manager/ Contractor's Representative : Office and Site based | Sum | 1 |  | 0
0
1.3.7 | Health, Safety and Environmental Officer | Sum | 1 |  | 0
0
1.3.8 | Site Supervisor / Planner : Office and Site based | Sum | 1 |  | 0
0
1.3.9 | Site Agent and SHE Representative: Site based | Sum | 1 |  | 0
0
1.3.10 | Comply with SHEQ requirements by Safety Officer e.g. regular review and update of Health and Safety File | Sum | 1 |  | 0
0
1.3.11 | Site offices cost , including ablution facilities, site administration, transport, accommodation etc. | Sum | 1 |  | 0
0
1.3.12 | Coordination and working together with other Contractors / Sub-Contractors / Nominated Sub-Contractors | Sum | 1 |  | 0
0
1.3.13 | Periodic medical, fitness and induction costs | Sum | 1.727 |  | 0
0
1.3.14 | Security for site camp and work on site | Sum | 1 |  | 0
0
1.3.14 | Local labour management cost for: | Sum | 1 |  | 0
0
1.3.14.1 | Overhead cost to manage SMME's that will execute a portion of the contract (30% of labour portion) | Sum | 1 |  | 0
0
1.3.14.2 | Community Liaison Officer (R 5000.00 p/month) | Sum | 1 |  | 0
0
1.3.14.3 | Community liaison and communication | Sum | 1 |  | 0
0
1.3.14.4 | Community and Labour desk for community liaison, communication, to receive complaints and enquiries, and |  |  |  | 0
| proactively manage relations | Sum | 1 |  | 0
0
1.3.14.5 | Employment of local people for the duration of the project (R 5000.00 p/month per worker) | Sum | 1 |  | 0
0
1.3.14.6 | Training of semi-skilled labourers | Sum | 1 |  | 0
0
1.3.14.7 | Management of local labourers | Sum | 1 |  | 0
0
1.4 | COMPLY WITH THE FOLLOWING SHEQ REQUIREMENTS- TIME RELATED |  |  |  | 0
1.4.1 | Monthly adherence to Construction Regulations of the OHS Act | Sum | 1 |  | 0
0
1.4.2 | Monthly review and update the Health and Safety Plan (H & S Plan) | Sum | 1 |  | 0
0
1.4.3 | Monthly review and update the Risk Assessment for activities (RA) | Sum | 1 |  | 0
0
1.4.4 | Monthly review and update the Environmental Management Plan (EMP) | Sum | 1 |  | 0
0
1.5 | ITEMS NOT COVERED ELSEWHERE |  |  |  | 0
1.5.1 | Servitude compensation | PC | 0 |  | 0
0
1.5.2 | Town planner - servitude registration process | PC | 0 |  | 0
0
1.5.3 | Pr. Land Surveyor - servitude registration at S.G. | PC | 0 |  | 0
0
1.5.4 | Attorney - servitude registration on deed | PC | 0 |  | 0
0
1.5.5 | Servitude compensation | PC | 0 |  | 0
0
1.5.6 | Standing time compensation for local labour | PC | 0 |  | 0
0
0
| TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES |  |  |  | 0

## LIST B - SITE WORK
ITEM | DESCRIPTION | REF | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL
2 | BULK EARTHWORKS | SANS 1200 |  |  |  |  | 0
2.1 | GENERAL | [5 empty] | 0
2.1.1 | Before starting the work the Contractor is to satisfy himself as to the accuracy of the Engineer’s drawings. | [5 empty] | 0
| All calculations will be based on this unless notified prior to site clearance and excavations commencing. | 1200 A | Sum | 1 |  |  | 0
0
2.2 | SITE CLEARANCE AND PREPARATION | 1200 D |  |  |  |  | 0
2.2.1 | Allow for clearing the areas and scarifying for trenches, ponds and roads of all grass, weeds, shrubs, trees | [5 empty] | 0
| trunks not exceeding 150 mm girth, builder’s rubble, premix, etc., including grubbing up all roots, scoffing up | [5 empty] | 0
| as required and carting away of all vegetation and debris. |  | m² | 1480 |  |  | 0
0
2.2.2 | Remove topsoil to nominal depth of 150 mm, stock pile and maintain. Stock pile site to be determined by | [5 empty] | 0
| Contractor. |  | m² | 1480 |  |  | 0
0
2.2.3 | Remove topsoil to a nominal depth of 600mm and dispose within a free haul distance of 5km |  | m² | 0 |  |  | 0 | Measured in Bulk Excavation
0
2.2.4 | Remove and grub large trees and tree stumps and spoil off site of girth of over 150 mm and up to 2 m |  | Sum | 0 |  |  | 0
0
2.2.5 | Remove and grub large trees and tree stumps and spoil off site of girth of over 2 m and up to 3 m |  | Sum | 0 |  |  | 0
0
2.2.6 | Remove and grub large trees and tree stumps and spoil off site of girth of over 3 m |  | Sum | 0 |  |  | 0
0
2.2.7 | Remove redundant foundations present on site. |  | Sum | 1 |  |  | 0
0
2.3 | BULK EXCAVATIONS | 1200 D |  |  |  |  | 0
| Note: Contractors are to note that the prices for the bulk excavations are to include for the formation of | [5 empty] | 0
| buttered banks required for lateral support and for ramps for the removal of excavated material and shall | [5 empty] | 0
| also include for all tests required. | [5 empty] | 0
0
2.3.1. | Bulk excavation and dispose within a free haul distance of 5 km, in all materials. |  | m³ | 334.08 |  |  | 0
0
2.3.2 | Bulk excavation and stockpile for use as backfill. (Refill of insitu material after earth grid installation) |  | m³ | 62.64 |  |  | 0
0
2.4 | EXTRA OVER BULK EXCAVATION | [5 empty] | 0
2.4.1. | Intermediate excavation |  | m³ | 50 |  |  | 0
0
2.4.2 | Hard rock excavation |  | m³ | 50 |  |  | 0
0
2.4.3 | Boulder excavation Class A |  | m³ | 50 |  |  | 0
0
2.4.4 | Boulder excavation Class B |  | m³ | 50 |  |  | 0
0
2.5 | SPECIAL WATER CONTROL | [5 empty] | 0
2.5.1 | Allow for keeping excavations free of water for the duration of the contract. |  | Sum | 1 |  |  | 0
0
2.6 | BULK BACKFILL & IMPORTING OF MATERIALS FROM COMMERCIAL SOURCES (INCL. | 8.3.4a |  |  |  |  | 0
| HAULING) | [5 empty] | 0
| Substation Platform | [5 empty] | 0
2.6.1 | Selected 400mm x 500mm "Building Sand" for earth grid. |  | m³ | 334.08 |  |  | 0
0
2.6.2 | Selected Grade G5 material compacted in layers 150mm thick to 90% Mod AASHTO to a moisture of | [5 empty] | 0
| of +-2% of optimum, including MOD tests on the material to be used and submitted for the | [5 empty] | 0
| engineer's approval (Measured tight). [IMPORT] |  | m³ | 244.24 |  |  | 0
0
2.6.3 | Rip and recompact 150mm insitu material to 90% Mod AASHTO. |  | m³ | 244.24 |  |  | 0
0
| Roadway (Inside Substsation) | [5 empty] | 0
2.6.4 | Selected Grade G3 wearing course material, compacted in layers 150mm thick to 98% Mod AASHTO | [5 empty] | 0
| to a moisture content of +-2% of optimum, including MOD tests on the material to be used and | [5 empty] | 0
| submitted for the engineer's approval (Measured tight). [IMPORT] |  | m³ | 20 |  |  | 0
0
2.6.5 | Rip and recompact 150mm insitu material to 90% Mod AASHTO. |  | m³ | 20 |  |  | 0
2.7 | GABIONS AND PITCHING | [5 empty] | 0
| Supply and install complete as per manufacturers specification-stone pitching or precast blocks or similar | [5 empty] | 0
2.7.1 | For embankment erosion control / light (grouted) pitching |  | m² | 0 |  |  | 0
0
2.8 | TOP SOILING | [5 empty] | 0
2.8.1 | Using material from stockpiles and placing 150 mm layer topsoil on embankments before grassing. | 8.3.10a | m³ | 0 |  |  | 0
0
2.8.2 | Spoil remaining of stock pile material. Spoil site to be determined by Contractor. |  | m³ | 0 |  |  | 0
0
2.8.3 | Top layer of 25mm stone dolomite or granite, 100mm thick layer. |  | m³ | 176.16 |  |  | 0
0
2.9 | TRANSPORT | [5 empty] | 0
| Disposal of burden to a site identified by the Contractor. | [5 empty] | 0
2.9.1 | Limited haul |  | m³ | 334.08 |  |  | 0
0
2.9.2 | Long haul |  | m³ | 50 |  |  | 0
0
2.10 | ADDITIONAL TESTS REQUESTED BY THE ENGINEER | [5 empty] | 0
| The Contractor is to allow in his rates for all density tests required to comply with relevant specifications and | [5 empty] | 0
| drawings and in order to ensure that the required densities are obtained. The Contractor shall only be paid | [5 empty] | 0
| under the following items for test over and above the required tests as specified by the Engineer to be done | [5 empty] | 0
| by an independent laboratory. | [5 empty] | 0
2.10.1 | DCP - Dynamic Cone Penetrometer test to be done on substation platform. Positions to be indicated by |  | Each | 4 |  |  | 0
| the Engineer | [5 empty] | 0
0
2.11 | EXCAVATION / BACKFILL | [5 empty] | 0
2.11.1 | Excavate all materials for trenches, backfill, compact and dispose of surplus material. |  | m³ | 20 |  |  | 0
0
2.11.2 | Excavate and dispose of unsuitable material in trench bottom |  | m³ | 20 |  |  | 0
0
2.11.3 | Grassing - regrass the area surrounding the substation. |  | m² | 2000 |  |  | 0
0
2.12 | HERBICIDES | [5 empty] | 0
2.12.1 | Application of Herbicides and Pesticides over the complete terrace (After terrace completion, during | [5 empty] | 0
| construction, before hand over and before lapse of 12 month maintenance period). |  | Each | 4 |  |  | 0
0
2.12.2 | Application of Herbicides and Pesticides over all gravel roads |  | Sum | 1 |  |  | 0
0
2.13 | SITE SURVEY | [5 empty] | 0
2.13.1 | As-built survey of the entire substation c/w foundation levels and section levels. |  | Sum | 1 |  |  | 0
0
2.14 | ACCESS ROAD GRADING | [5 empty] | 0
2.14 | Use stockpiled material (from 2.2.2) to regrade the existing access road to the substation. Soil to be
| compacted to 90% Mod AASHTO. |  | m³ | 1480 |  |  | 0
| TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [5 empty] | 0

## LIST C - EARTH GRID
ITEM | DESCRIPTION | REF | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL
3.1 | INSTALLATION OF EARTH GRID | VE9335-6-EARTH |  |  |  |  | 0
| METHOD: Earth grid to be excavated and installed when the terrace / platform is 600 mm below finished | [5 empty] | 0
| level. Grid to be clearly marked with reference pegs following the installation. Tails to be marked and | [5 empty] | 0
| protected during backfilling of terrace layers. | [5 empty] | 0
3.1.1 | Setting out and maintaining of longitudinal and transverse stakes indicating earth grid layout & level |  | Sum | 1 |  |  | 0
0
3.1.2 | Performing cross-cuts to determine the position of the existing substation earth grid |  | Sum | 1 |  |  | 0
0
3.2 | SUPPLY AND INSTALL COMPLETE EARTH GRID | [5 empty] | 0
| Note: Copper quantified is for the earth grid only, and not for the earthing of the hold-down bolts. Copper | [5 empty] | 0
| for holding down bolts to be priced and allowed for with the foundations. | [5 empty] | 0
3.2.1 | 10 mm dia. round Copper main earth grid 1 m below final level. | D-DT-5240 | m | 650 |  |  | 0
0
3.2.2 | 10 mm dia. Copper equivalent CAMO CCS |  | m | 200 |  |  | 0
0
3.2.3 | 150 mm² Copper Equivalent CAMO CCS |  | m | 0 |  |  | 0
0
3.2.4 | 50 mm x 3 mm flat copper for earth tails connected to the earth grid and equipment foundation and all | [5 empty] | 0
| building and foundation reinforcing as shown on drawing VE9335-6-EARTH | D-DT-5240 | m | 93.9038 |  |  | 0
0
3.2.5 | 50 mm x 3 mm flat copper for earth tails to the fence and fence corner gate post (CGP). | D-DT-5240 | m | 20 |  |  | 0
0
3.2.6 | 50 mm x 3 mm flat copper for earthing and earth-tails for building earthing of panels. This earthing should run | [5 empty] | 0
| in the cable trench / cable rack. | D-DT-5240 | m | 0 |  |  | 0
0
3.2.7 | 50 mm x 3 mm flat copper for earthing and earth-tails for equal potential foot plates. | D-DT-5240 | m | 22 |  |  | 0
0
3.2.8 | Sacrificial earth anode | D-DT-5240 | Each | 0 |  |  | 0
0
3.2.9 | 1 x 16 mm dia, 2 m deep earth spike |  | Each | 0 |  |  | 0
0
3.2.10 | 2 x 16 mm dia, 2 m deep earth spike in a 100 mm predrilled hole and backfilled with conductive concrete | [5 empty] | 0
| (provisional) |  | Each | 10 |  |  | 0
0
3.2.11 | 2 x 16 mm dia, 30 m deep earth spike in a 100 mm predrilled hole and backfilled with conductive concrete | [5 empty] | 0
| (provisional) |  | Each | 6 |  |  | 0
0
3.2.12 | 1 x 10 mm dia, 5 m deep earth rod in a 200 mm predrilled hole and backfilled with a Bentonite slurry mixture | [5 empty] | 0
| (provisional) |  | Each | 18 |  |  | 0
0
3.2.13 | Transformer earthing, 80 mm x 6 mm galvanised steel earth strap (to be measured and bent on site) | D-DT-5232 | m | 30 |  |  | 0
0
3.2.14 | Insulated Earth 10 mm Round to earth bar inside buildings (to pass through Roxtec seals) |  | m | 0 |  |  | 0
0
3.2.15 | Equal potential foot plate |  | Each | 11 |  |  | 0
0
3.3 | JOINTS AND BONDING - ALL FOUNDATION COPPER TO MAIN EARTH GRID | [5 empty] | 0
3.3.1 | Main earth grid bonding 10 mm round to 10 mm round. | D-DT-5240 | Each | 110 |  |  | 0
0
3.3.2 | Main earth bonding to earth tails diameter 10 mm to 50 x 3 mm flat. |  | Each | 118 |  |  | 0
0
3.3.3 | Flat tail bonding 50 x 3 mm to 50 x 3 mm (foundations). | D-DT-5240 | Each | 84 |  |  | 0
0
3.3.4 | Flat tail bonding 50 x 3 mm to equal potential foot plates. | D-DT-5240 | Each | 22 |  |  | 0
0
3.3.5 | Flat tail bonding 50 x 3 mm to fence and corner gate post. |  | Each | 12 |  |  | 0
0
3.3.6 | Main earth bonding to the existing substation earth grid. |  | Each | 20 |  |  | 0
0
3.4 | EXCAVATION & BACKFILL | [5 empty] | 0
| After the substation terrace is excavated to -600mm, then 400mm wide trenches shall be excavated to | [5 empty] | 0
| -1100mm for the earth grid installation at -1000mm. | [5 empty] | 0
| Excavate, backfill and compaction of trenches for Earthgrid (Earth grid level 1100mm below finished | [5 empty] | 0
| substation level) for: | [5 empty] | 0
3.4.1 | i) 10 mm round copper. |  | m | 680 |  |  | 0
0
3.4.2 | ii) 50 mm x 3 mm flat copper |  | m | 94.4 |  |  | 0
0
3.4.3 | ii) Excavate and backfill of imported soil for earthing. |  | m | 67.2 |  |  | 0
0
3.5 | Design and Testing | [5 empty] | 0
| It is the responsibility of the Substation Contractor to test the earth grid resistance on completion of the earth | [5 empty] | 0
| mat. | [5 empty] | 0
3.5.1 | The results shall be certified by an independent third party and compared to the design values. |  | Sum | 1 |  |  | 0
0
3.5.2 | Investigation and recommendation by specialist if earth resistance measures > 1 Ω |  | Sum | 1 |  |  | 0
0
0
0
| TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [5 empty] | 0

## LIST D - FENCING
ITEM | DESCRIPTION | REF | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL
4 | STEEL FENCING | [5 empty] | 0
4.1 | SUBSTATION FENCING (NEW) | [5 empty] | 0
| Supply and install new diamond-mesh and electrical substation fence (2.4m high fence). | [5 empty] | 0
All binding/strain wire and required nuts/bolts/washers to be supplied with the fence.
4.1.1 | Galvanised posts, taper locking post including locking recess mechanism, posts sealed with a UV stabilized
| polymer cap. (3.6 m high, tapering 85 mm to 45 mm, with depth of 85 mm). |  | Each | 0 |  |  | 0
0
4.1.2 | Posts for safety fence (2.4m) (Intermediate Post) | D-DT-5237s5A | Each | 11 |  |  | 0
0
4.1.3 | Posts for safety fence (2.4m) (Corner Post) | D-DT-5237s5A | Each | 1 |  |  | 0
0
4.1.4 | Diamond mesh fence class A (1.8 m high). | D-DT-5237s5A | m | 80 |  |  | 0
0
4.1.5 | Razor wire flat wrap - 500mm class A (meters of fence to cover) | D-DT-5237s5A | m | 80 |  |  | 0
0
4.1.6 | Diamond mesh (1.8m high) security gate - 5m (including gate post and post struts) | D-DT-5237s5A | Each | 3 |  |  | 0
0
4.1.7 | Diamond mesh (1.8 m high) pedestrian swing gate (including gate post and post struts) | D-DT-5237s5A | Each | 0 |  |  | 0
0
4.1.8 | Fence anti-tunnelling (excludes area underneath 5m security gates) | D-DT-5237s5A | m | 65 |  |  | 0
0
4.1.9 | Fence curbing | SANS 927 FIG 3 | m | 85 |  |  | 0
0
4.2 | SUBSTATION FENCING (EXISTING) | [5 empty] | 0
| Remove the portion of the existing fence. | [5 empty] | 0
4.2.1 | Remove the existing fence, posts and curbing as indicated. | VE9335-6-GA | m | 65 |  |  | 0
0
4.2.2 | Modify existing corner post to strainer post (for the construction of the new fence from the existing fence) |  | Each | 2 |  |  | 0
0
4.2.3 | Remove the existing security gate - 5m |  | Each | 3 |  |  | 0
0
4.2.3 | Delivery of removed fence & gate to Vaalpark CNC |  | Each | 3 |  |  | 0
0
0
0
0
0
0
0
0
0
| TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [5 empty] | 0

## LIST E - CIVIL WORK
ITEM | DESCRIPTION | REF | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL
5 | CIVIL WORKS | SANS 1200
5.1 | GENERAL
5.1.1 | Before starting the work the Contractor is to satisfy himself as to the accuracy of the Engineer’s drawing.
| All calculations will be based on this unless notified prior to site clearance and excavations commencing. | 1200 A | Sum | 1 |  |  | 0
0
5.2 | FOUNDATIONS / PLINTHS | 1200LC |  |  |  |  | 0
| Excavate, dispose of burden within free haul distance of 5km, backfill, compaction, supply and cast complete | [5 empty] | 0
| concrete foundations with holding down bolts, fdn, with holding down bolts, fdn, internal earthing and earth | [5 empty] | 0
| connections detailed in the drawings, Rates for concrete to include for taking concrete to include for taking | [5 empty] | 0
| concrete samples and obtain test certificates for 9,14 & 28 days. General rules applicable to casting of | [5 empty] | 0
| concrete: cast below 35°C; use steel shuttering as far as possible, use slow curing concrete; use low shrinking | [5 empty] | 0
| concrete. Concrete maximum shrinkage, stress and modules of elasticity obtainable from the specification. | [5 empty] | 0
| Only steel shuttering may be used | [5 empty] | 0
5.2.1 | 132kV Isolator Support Foundation (Type 3) (2.4m Phase Spacing) | 5202s1e | Each | 3 |  |  | 0
0
5.2.2 | Tube Busbar Supt. Fdn. 132kV | 5208s1 | Each | 6 |  |  | 0
0
5.2.3 | 132kV Circuit Breaker Foundation (Type 2) | 5200s1C | Each | 1 |  |  | 0
0
5.2.4 | Med. Equip. Supt. Foundation For Current Transformer | 5206s1 | Each | 3 |  |  | 0
0
5.2.4.1 | Standard Transformer Plinth 5-20MVA | 5231s1 | Each | 1 |  |  | 0
5.2.4.2 | Standard Transformer Slipway As Per D-DT | 5231s1 & |  |  |  |  | 0
|  | VE9335-6-FDN | Each | 1 |  |  | 0
5.2.4.3 | Standard Self Contained Oil Containment Area | 5232s2B | Each | 1 |  |  | 0
0
5.2.5 | NEC/NER/Aux TRFR 33/22/11kV Foundation | 5207s1b | Each | 1 |  |  | 0
0
5.2.6 | 6.6kV-44kV Post Insulator Support Fdn | 5221s1 | Each | 2 |  |  | 0
0
5.2.7 | Bkr. 22kV Foundation Details | 5214s1a | Each | 3 |  |  | 0
0
5.2.8 | Isolator 22kV Supt Foundation | 5205s1 | Each | 7 |  |  | 0
0
5.2.9 | Column Supt. Foundation | 5223s2 | Each | 6 |  |  | 0
0
5.2.10 | Med. Equip. Supt. Foundation (132kV CT) | 5206s1 | Each | 3 |  |  | 0
0
5.2.11 | Med. Equip. Supt. Foundation (22kV VT) | 5206s1 | Each | 1 |  |  | 0
0
5.2.12 | Lighting-Lightning Mast 21 M Tubular Support Foundation (1 x Provisional) | 5217s6 | Each | 3 |  |  | 0
0
5.2.13 | Steel Templates For The Above Holding Down Bolts - To Be Approved Prior To Foundation Construction |  | Sum | 1 |  |  | 0
5.2.14 | Lighting-Lightning Mast 14 M Tubular Support Foundation (Provisional) | 5217s1B | Each | 3
0
5.3 | CABLE DUCTS AND COVERS | 1200LC |  |  |  |  | 0
| Excavate, dispose of burden within free haul distance of 5km, backfill, compaction, supply and cast/erect | [5 empty] | 0
| complete concrete walls c/w covers detailed in the drawings (NOTE: 1.2m.K/W bedding to be used | [5 empty] | 0
| for power cables) | [5 empty] | 0
5.3.1 | Complete 600 mm wide cable trenches as per drawing | D-FS-887 | m | 47 |  |  | 0
0
5.3.2 | Complete cable road duct (8 x 150mm uPVC pipe duct) complete with brick wall and sloped entry. | D-DT-5254-3d | Sum | 1 |  |  | 0
Supply and install 76 x 38 x 6.7 TF channels to support the D-FS-887 trench covers over the cable
entry section as per drawing VE9335-6-FDN.
0
5.3.3 | Supply and install non-metallic draw wires in all PVC ducts. A surplus of the non-metallic draw wire |  | Each | 8
of at least 2m shall be left at each end of the ducts.
5.3.4 | Supply, transport and install end caps for both ends of all the installed cable road ducts. The |  | Each | 8
contractor shall ensure that the non-metalic draw wire is inside the duct, the duct shall be clean, water
and vermin proof.
5.3.5 | The uPVC cable ducts shall be encased with concrete and shall have a minimum surround of 75mm, |  | Sum | 1
to prevent collapsing or deformation after backfilling.
5.3.6 | Extra over 600mm wide cable trench for: | [5 empty] | 0
5.3.6.1 | Closed end |  | Each | 2 |  |  | 0
0
5.3.7 | Extra over excavations for: | [5 empty] | 0
5.3.7.1 | Intermediate excavation |  | m³ | 1 |  |  | 0
5.3.7.2 | Hard rock excavation |  | m³ | 1 |  |  | 0
0
5.4 | FENCE/GATE FOUNDATION AND CURBING | [5 empty] | 0
5.4.1 | Fence Foundations - Diamond Mesh | 5237s5A | Each | 12 |  |  | 0
5.4.2 | Gate Concrete Foundation | 5237s3 | Each | 3 |  |  | 0
5.4.3 | Remove the existing fence curbing and anti-tunneling. |  | m | 83 |  |  | 0
5.4.4 | Remove existing gate ramp foundations |  | Each | 3 |  |  | 0
0
5.5 | ROAD CURBING | [5 empty] | 0
5.5.1 | Substation road curbing | SANS 927 FIG 3 | m | 42 |  |  | 0
0
| TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [5 empty] | 0

## LIST F - BUILDINGS
ITEM | DESCRIPTION | REF | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL
6 | FACILITIES
6.1 | REPAIRS TO EXISTING 88 kV CONTROL ROOM | [5 empty] | 0
0
6.1.1 | Supply and installation of plasterboard ceilings in existing control room. |  | m² | 22 |  |  | 0
0
6.1.2 | Supply and installation of new fluorescent light fixture and tubes ( 2 x 5ft tubes, 58W per tube) |  | ea | 1 |  |  | 0
0
6.1.3 | Relocation of the existing control room DB. |  | ea | 1 |  |  | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
[8 empty] | 41 | 41
| TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [5 empty] | 0

## LIST G - STEELWORK
ITEM | DESCRIPTION | REF | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL
7 | ERECTION OF STEELWORK
Equipment Support - Manufacture, supply and install equipment support for the following:
Manufacture, supply and install equipment support for the following:
| Isolator 132kV 2500A 25kA Bull - Bussection | 4630s1
7.1 | Isolator Std 132kV Manual Lattice Support - 2.4m Phase Crs | 5202s2K | Each | 2 |  |  | 0
0
| Non Extendable Busbar 132kV Onto Bussection | 4655s2 |  |  |  |  | 0
7.2 | 66/132kV Tubular Busbar Support | 5208s2 | Each | 6 |  |  | 0
0
| Isolator 132kV 2500A 25kA Cent - Trfr Bay | 4623s1 |  |  |  |  | 0
7.3 | Isolator Std 132kV Manual Lattice Support - 2.4m Phase Crs | 5202s2K | Each | 1 |  |  | 0
0
| Breaker 132kV 3150A 40kA Cent | 4618s1 |  |  |  |  | 0
7.4 | Circuit Breaker - 132kV Tubular Support Steelwork | 5200s2a | Each | 1 |  |  | 0
0
| Current Transformer 132kV 2500A 25kA 2P2M2B | 4631s1 |  |  |  |  | 0
7.5.1 | Medium Equipment Support Cap M1 Adjustable Fixing Centres | 5206s5 | Each | 3 |  |  | 0
7.5.2 | Medium Equipment Support Steelwork 2.5m High | 5206s3 | Each | 3 |  |  | 0
0
| Transformer 88/22kV 10 MVA OLTC Cent To Bull | 4608 |  |  |  |  | 0
7.5.3 | Transformer Aux Cable Rack (Max.) | 5231s1C | m | 8 |  |  | 0
0
| NEC/NER/Aux Transformer 22kV 360A Bull | 4613 |  |  |  |  | 0
7.6 | NECR'T/Aux. Trfr 6.6-22kV Lattice Support - 1.5m | 5207s2A | Each | 1 |  |  | 0
0
| 22kV Road Crossing | 4801s1 |  |  |  |  | 0
7.7 | 1200 Phase Centres, High Level, Lipped Channel Support - Type A | 5221s2 | Each | 2 |  |  | 0
0
| Trfr Breaker 22kV 1250A 20kA Bull (Combo-Units) (CTB36 Outdoor CB With CT) | 5216 |  |  |  |  | 0
7.8.1 | Bkr. 22kV Steel Support | 5216s2B | Each | 1 |  |  | 0
7.8.2 | Bkr. Structure Height Adapter (790mm) | 5216s2B | Each | 1 |  |  | 0
0
| Isolator 22kV 2500A 25kA Bull - Transformer Bay | 4626s1 |  |  |  |  | 0
7.9 | Isolator 22kV Supt. | 5205s2A | Each | 1 |  |  | 0
0
| Mv Busbar 22kV Bull Basic Bay | 4755s3 |  |  |  |  | 0
7.10 | Mv Box Structure Standard Steelwork (Without Busbar/Bay Isolator Channels) with "Heavy" C2 column | 5223s6 | Each | 1 |  |  | 0
as specified in D-DT-5223s3
0
| Mv Busbar 22kV Bull Ext Bay | 4755s4 |  |  |  |  | 0
7.11 | Mv Box Structure Standard Steelwork (Without Busbar/Bay Isolator Channels) with "Heavy" C2 column | 5223s6 | Each | 1 |  |  | 0
| as specified in D-DT-5223s3 | [5 empty] | 0
| Isolator 22kV 2500A 25kA Bull - Bussection | 5223s6 |  |  |  |  | 0
7.12 | Isolator 22kV Supt. | 5205s2A | Each | 2 |  |  | 0
0
| Isolator 22kV 2500A 25kA Centipede - Breaker Isolator | 5223s6 |  |  |  |  | 0
7.13 | Isolator 22kV Supt | 5205s2 | Each | 2 |  |  | 0
0
| Fdr Breaker 22kV 1250A 20kA Centipede (Combo-Units) (CTB36 Outdoor CB With CT) | 5216 |  |  |  |  | 0
7.14.1 | Bkr. 22kV Steel Support | 5216s2B | Each | 2 |  |  | 0
7.14.1 | Bkr. Structure height adapter (790mm) | OEM | Each | 2
0
| Isolator 22kV 2500A 25kA Centipede - Feeder Isolator | 4626s1 |  |  |  |  | 0
7.15 | Isolator 22kV Supt | 5205s2 | Each | 2 |  |  | 0
0
| Voltage Transformer 22kV/110V | OEM |  |  |  |  | 0
7.16.1 | Medium Equipment Support Cap M1 Adjustable Fixing Centres | 5206s6 | Each | 1 |  |  | 0
7.16.2 | Medium Equipment Support Steelwork 2.5m High | 5206s3 | Each | 1 |  |  | 0
0
| Substation Lighting Mast 21m | [5 empty] | 0
7.17 | Lighting-Lightning Mast 21m Tubular Support Steelwork (1 x Provisional) | 5217s2E | Each | 3 |  |  | 0
0
| Steel Fire Barrier | [5 empty] | 0
7.18.1 | Steel Fire Barrier - Module A & B | 5218s2A | Each | 2 |  |  | 0
7.18.2 | Steel Fire Barrier - Lattice Support | 5218s2A | Each | 3 |  |  | 0
0
| Provisional Substation Lighting Mast 14m | [5 empty] | 0
7.19 | Lighting-Lightning Mast 14m Tubular Support Steelwork (Provisional) | 5217s2D | Each | 3 |  |  | 0
0
0
0
0
0
0
0
0
0
0
0
0
| TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [5 empty] | 0
LV AUXILIARY SUPPLY (Sicelo Substation)
The supply at Sicelo Substation will come from the Midvaal Switchgear Room

## LIST H - EQUIPMENT
ITEM | DESCRIPTION | REF | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL
8 | INSTALLATION OF EQUIPMENT
8.1 | SUPPLY, INSTALLATION AND COMMISSIONING OF THE FOLLOWING EQUIPMENT
(Tenderer to allow for cost of commissioning by the OEM or accredited agency):
8.1.1 | Isol 132kV 2500A 25kA CRDB H/O 31mm (2.4m Phase Spacing) | 6150s1 | Each | 3 |  |  | 0
0
8.1.2 | Circuit Breaker 132kV 3150 40kA 3P, 31mm/kV | 6250 | Each | 1 |  |  | 0
0
8.1.3 | CT 132kV 2500A 40kA 2P2M2B (500) | 6190s1 | Each | 3 |  |  | 0
0
8.1.4 | 88 kV / 110V Voltage Transformer 100VA. | D-DT-6171 | Each | 0 |  |  | 0
0
8.1.5 | Transformer 10MVA 88/22kV OLTC Ynd1, 31mm/kV | 6128 | Each | 1 |  |  | 0
0
8.1.6 | NEC/NER/AUX Transformer 22kV 360A 100kVA 22kV/420/240V 31mm/kV | 6141 | Each | 1 |  |  | 0
0
8.1.7.1 | CTB36 Outdoor Vacuum CB | 6252 | Each | 3 |  |  | 0
8.1.7.2 | Composite CT - 1200/800/200/1A Class 0.2 | OEM | Each | 9 |  |  | 0
8.1.7.3 | 22kV Surge Arrestor & Assembly | 0261s1 | Each | 9 |  |  | 0
0
8.1.8 | Isolator 22kV 2500A 25kA CRDB H/O 31mm/kV | 6154s2 | Each | 7 |  |  | 0
0
8.1.9 | 22kV MV Bull Basic Bay Equipment (Clamp Pistol, Long Rod Insul, Line Post Insul Etc.) | 4755s3 | Each | 1 |  |  | 0
0
8.1.10 | 22kV MV Bull Ext Bay Equipment (Clamp Pistol, Long Rod Insul, Line Post Insul Etc.) | 4755s4 | Each | 1 |  |  | 0
0
8.1.11 | VT 1 Ph 22kV/110V 100/50VA | 6173 | Each | 3 |  |  | 0
0
8.1.12 | Insul Post Stn 132kV | 6230 | Each | 6 |  |  | 0
0
8.1.13 | Insul Post Stn 22kV | 6235 | Each | 6 |  |  | 0
0
8.1.14 | S/Arr S/Cl 88kV MCOV 56kV | 6211 | Each | 3 |  |  | 0
0
8.1.15 | S/Arr S/Cl 22kV MCOV 24kV | 6215 | Each | 12 |  |  | 0
0
8.1.16 | S/Arr S/Cl 66kV MCOV 48kV | 6212 | Each | 1 |  |  | 0
0
8.2 | Testing And Commissioning By Oem On Site | [5 empty] | 0
8.2.1 | 132 kV Isolator |  | Sum | 3 |  |  | 0
0
8.2.2 | 132 kV Current Transformer |  | Sum | 1 |  |  | 0
0
8.2.3 | 132 kV Circuit Breaker |  | Sum | 1 |  |  | 0
0
8.2.4 | 88/22 kV Power Transformer |  | Sum | 1 |  |  | 0
0
8.2.5 | 22 kV NECR/T |  | Sum | 1 |  |  | 0
0
8.2.6 | 22kV Outdoor Circuit Breaker With Current Transformer |  | Sum | 3 |  |  | 0
0
8.2.7 | 22kV Isolator |  | Sum | 7 |  |  | 0
0
8.2.8 | 22kV Voltage Transformer (1 x New Set & 1 x Existing Set) |  | Sum | 6 |  |  | 0
0
8.2.9 | Yard AC Distribution Board And Interface Box |  | Sum | 1 |  |  | 0
0
8.3 | FACTORY ACCEPTANCE TEST (FAT) | [5 empty] | 0
| Provision For Three (3) Engineer And Three (3) Employer Representatives And One (1) Contractor | [5 empty] | 0
| Representatives To Witness FAT At Manufacturer As Specified In Clause 1.4 (L) For The Following | [5 empty] | 0
| Equipment: | [5 empty] | 0
8.3.1 | 10 MVA 88/22 kV Ynd1 Transformers I |  | Sum | 1 |  |  | 0
8.3.2 | 22 kV NEC Transformer |  | Sum | 1 |  |  | 0
0
8.4 | Clamp Assemblies, Stringing, Stranded Conductor & Tubular Conductor | [5 empty] | 0
| Supply And Install The Following Which Must Be Capable Of Carrying 650 A: | [5 empty] | 0
8.4.1 | Clamp, Tube TBSS 120/127 | 6118s1 | Each | 3 |  |  | 0
0
8.4.2 | Clamp, Tube TBC 120/120 | 6116 | Each | 3 |  |  | 0
0
8.4.3 | Clamp B/Comp 26.5mm-38mm 0Dg EXC-B (KC2) | 6006s2 | Each | 12 |  |  | 0
0
8.4.4 | Clamp Peg Al Cent 26.5mm EPC-26 | 6115s1 | Each | 21 |  |  | 0
0
8.4.5 | Clamp B/Comp 26.5mm Palm 0Dg EPC-A | 6018 | Each | 21 |  |  | 0
0
8.4.6 | Clamp B/Comp 26.5mm Palm 45Dg EPC-B | 6018 | Each | 15 |  |  | 0
0
8.4.7 | Clamp Cross 26.5mm - 26mm K2 EX-B | 6002s2 | Each | 6 |  |  | 0
0
8.4.8 | Clamp B/Comp 26.5mm-26mm 0Dg EXC-A (KC1) | 6006s1 | Each | 3 |  |  | 0
0
8.4.9 | Clamp B/Comp 38.3mm-38mm 0Dg EXC-C (KC3) | 6006s3 | Each | 9 |  |  | 0
0
8.4.10 | Clamp Cross 16.3mm - 38mm K3 EX-C | 6002s3 | Each | 6 |  |  | 0
0
8.4.11 | Clamp T/Comp 26.5mm - 38.3mm 0Dg | 6010s4 | Each | 6 |  |  | 0
0
8.4.12 | Lug Al Hornet 1B M12 0Dg | 3074s1 | Each | 12 |  |  | 0
0
8.4.13 | Clamp T S/Comp TBCT-120/38C1 0Dg | 6090 | Each | 9 |  |  | 0
0
8.4.14 | Clamp Bus Coupler TBFC120-76 | 6086s1 | Each | 3 |  |  | 0
0
8.4.15 | Clamp Bus Coupler TBSC120-76 | 6086s2 | Each | 3 |  |  | 0
0
8.4.16 | End Cap TBEC 120 With F/Clamp | 6040s2 | Each | 6 |  |  | 0
0
8.4.17 | End Cap TBEC 120 Plain No F/Clamp | 6040s1 | Each | 6 |  |  | 0
0
8.4.18 | Clamp B/Comp 38.3mm Palm 0Dg EPC-D | 6018s3 | Each | 3 |  |  | 0
0
8.4.19 | Clamp B/Comp 38.3mm - 38mm 45Dg EXC-E (Kc4) | 6006s4 | Each | 6 |  |  | 0
0
8.4.20 | Clamp Peg Al Bull 38.3mm EPC 38 | 6115 | Each | 24 |  |  | 0
0
8.4.21 | Clamp T/Comp 38.3mm - 38.3mm 0Dg TC10 | 6010s2 | Each | 6 |  |  | 0
0
8.4.22 | Clamp Tub Tap-Off TBTC 120/C1-26 | 6119 | Each | 3 |  |  | 0
0
8.4.23 | Clamp Bus Coupler TBFC 120-127 | 6086s2 | Each | 3 |  |  | 0
0
8.4.24 | Clamp T S/Comp TBCT 80/38C1 45Dg | 6090s2 | Each | 3 |  |  | 0
0
8.4.25 | Clamp Cross 26.5mm - 38mm K4 EX-C | 6002s3 | Each | 6 |  |  | 0
0
8.4.26 | Clamp B/Comp 26.5mm-38mm 45Dg EXC-F | 6006s3 | Each | 0 |  |  | 0
0
8.4.27 | Clamp EUT-C 18.8mm - 26.5mm (Chicadee-Centipede) | 6099 | Each | 6 |  |  | 0
0
8.4.28 | Clamp EUT-D 26.5mm - 18.1mm (Centipede-Hornet) | 6099 | Each | 6 |  |  | 0
8.4.29 | Clamp B/COMP 38.3mm PALM 45DG EPC-E | 6018s3 | Each | 18 |  |  | 0
0
8.4.30 | Clamp B/COMP 26.5mm PALM 90DG EPC-C | 6018s3 | Each | 6 |  |  | 0
8.5 | Miscellaneous Assemblies | [5 empty] | 0
8.5.1 | Clevis Ball 16mm IEC 120kN | 6059s1 | Each | 21 |  |  | 0
0
8.5.2 | Sock Tongue 16mm IEC 120kN | 6061s1 | Each | 15 |  |  | 0
0
8.5.3 | Ball Joint For Portable Earth 20kA | 6081s1 | Each | 57 |  |  | 0
0
8.5.4 | Bracket, Control Cable | 6065s1 | Each | 11 |  |  | 0
0
8.5.5 | Clamp Cover Acrylic ACC4 | 6055s1 | Each | 3 |  |  | 0
0
8.5.6 | Putty, Scotchfill 38mm W Roll | 6292s1 | Each | 9 |  |  | 0
0
8.5.7 | Tape, Elect Epr 18W X 0,76 Thk | 6292s1 | Each | 15 |  |  | 0
0
8.6 | STRINGING, STRANDED CONDUCTOR & TUBULAR CONDUCTOR | [5 empty] | 0
| Supply and install the following tube and conductor: | [5 empty] | 0
8.6.1 | 22kV Road Crossing- Aluminium Tube 120 x 4 mm x 10 m. | 6000s1 | Each | 3 |  |  | 0
0
8.6.2 | 132 kV Busbar - Aluminium Tubes, 120 x 4 mm thick x 10 m lengths excl. Centipede vibration damping. | 6000s1 | Each | 3 |  |  | 0
| Centipede vibration damping measured in 8.6.3. | [5 empty] | 0
0
8.6.3 | Stringers and droppers - Hornet |  | m | 26 |  |  | 0
0
8.6.4 | Stringers and droppers - Centipede |  | m | 104 |  |  | 0
0
8.6.5 | Stringers and droppers - Centipede Insulated |  | m | 82 |  |  | 0
0
8.6.6 | Stringers and droppers - Bull |  | m | 125 |  |  | 0
0
8.6.7 | Stringers and droppers - Bull Insulated |  | m | 32 |  |  | 0
0
8.7 | PORTABLE EARTH | [5 empty] | 0
8.7.1 | Supply portable earths suitable for earth balls. |  | Set | 0 |  |  | 0
8.7.2 | Supply link stick |  | Set | 0 |  |  | 0
0
8.8 | PIPES | [5 empty] | 0
8.8.1 | Supply and install μPVC pipes, 50 mm diameter for lighting circuits |  | m | 60 |  |  | 0
8.8.2 | Supply and install nextube pipes, 110 mm diameter for transformer bays |  | m | 0 |  |  | 0
0
8.9 | LIGHTING / LIGHTNING MASTS | [5 empty] | 0
| Supply and install the following: | [5 empty] | 0
8.9.1 | FLOODLIGHT LED 90W, 10 800 LM, 120LM/W, FLT conforming to Eskom Standard 240-113163905. | 6009s1 | Each | 0 |  |  | 0
| Note: All masts to be supplied complete with wiring and circuit breaker etc. as per drawing. | [5 empty] | 0
8.9.2 | FLOODLIGHT LED 60W, 7 200 LM, 120LM/W, FLT conforming to Eskom Standard 240-113163905. | 6009s1 | Each | 12 |  |  | 0
| Note: All masts to be supplied complete with wiring and circuit breaker etc. as per drawing. (Provisional) | [5 empty] | 0
8.9.3 | Supply, make off and install 4c x 10 mm² cable for lighting |  | m | 120 |  |  | 0
0
8.10 | LABELS | [5 empty] | 0
| Supply and install the following signs to security fence: | [5 empty] | 0
8.10.1 | Prohibitive |  | Each | 4 |  |  | 0
0
8.10.2 | Unauthorised Entry and Interfering |  | Each | 6 |  |  | 0
0
8.10.3 | Hard hat area |  | Each | 3 |  |  | 0
0
8.10.4 | Substation name & owner at all new gates "ESKOM 88/22 kV Vaaldam Substation" |  | Each | 3 |  |  | 0
0
8.10.5 | Gate number |  | Each | 3 |  |  | 0
0
8.10.6 | In case of Emergency |  | Each | 4 |  |  | 0
0
8.10.7 | Equipment Label, size: Label 3 as per Eskom D-DT | 5047 | Each | 22 |  |  | 0
8.10.8 | Equipment Label, size: Label 4 as per Eskom D-DT | 5047 | Each | 35 |  |  | 0
8.10.9 | Equipment Label, size: Label 5 as per Eskom D-DT | 5047 | Each | 111 |  |  | 0
0
8.11 | CLOSING SPAN | [5 empty] | 0
8.11.1 | Supply and install the closing spans from the existing Themba Khubeka OHL (double circuit Chickadee) to the |  | Each | 2 |  |  | 0
| substation 22kV feeder bays. | [5 empty] | 0
8.12 | TEMPORARY CONNECTION REMOVAL | [5 empty] | 0
8.12.1 | Remove the temporary connection between the Themba Khubeka OHL and the "Gevangenis" feeder line. |  | Sum | 1
0
| TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [5 empty] | 0

## LIST I - CONTROL PLANT
ITEM | DESCRIPTION | REF | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL
9 | CONTROL CABLE WORK
Supply, installation and commissioning of the following control cables:
9.1 | CABLE LAYING
9.1.1 | Cable 1 kV 4c 4.0 mm² Armoured, Cu |  | m | 660 |  |  | 0
9.1.2 | Cable 1 kV 12c 4.0 mm² Armoured, Cu |  | m | 360 |  |  | 0
0
9.1.3 | Cable 1 kV 19c 4.0 mm² Armoured, Cu |  | m | 300 |  |  | 0
0
9.1.4 | Cable 10 Pair Telecommunication Cable (TPH 10 AX) |  | m | 100 |  |  | 0
9.1.5 | Cable 25 Pair Telecommunication Cable (TPH 25 AX) |  | m | 200 |  |  | 0
9.1.6 | BVX 4 ECV Cable Gland Adjust No.1 |  | Each | 20 |  |  | 0
9.1.7 | BVX 12 ECV Cable Gland Adjust No.3 |  | Each | 20 |  |  | 0
9.1.8 | BVX 19 ECV Cable Gland Adjust No.4 |  | Each | 20 |  |  | 0
9.1.9 | Cable Shroud for Gland No.1 |  | Each | 20 |  |  | 0
9.1.10 | Cable Shroud for Gland No.3 |  | Each | 20 |  |  | 0
9.1.11 | Cable Shroud for Gland No.4 |  | Each | 20 |  |  | 0
9.1.12 | Cable 4 Pair, 24AWG, Screended, RS485 cable (BELDEN#9844) |  | m | 100
0
9.2 | CABLE MAKE OFF | [5 empty] | 0
| Supply, making off and commissioning of cable ends. | [5 empty] | 0
9.2.1 | Cable 1 kV 4c 4 mm² Armoured, Cu |  | Each | 20 |  |  | 0
9.2.2 | Cable 1 kV 12c 4 mm² Armoured, Cu |  | Each | 20
9.2.3 | Cable 1 kV 19c 4 mm² Armoured, Cu |  | Each | 20
9.2.4 | Cable Ferrule as per Control Plant cabling and cable block diagrams |  | Sum | 1
0
9.3 | TESTING AND COMMISSIONING | [5 empty] | 0
9.3.1 | Megger testing of all LV cables before energising and confirming their destination |  | Sum | 1 |  |  | 0
0
9.4 | CONTROL PANELS (INDOOR SWING FRAME) | [5 empty] | 0
| Design, supply, install and commission panels as follows. | [5 empty] | 0
9.4.1 | 88/22 kV Transformer Protection and Tap Change Panel - 48U swing frame panel with 4TM7101 | D-DT-5413 | Each | 1 |  |  | 0
| transformer protection scheme & 4TC5200 tap-change scheme. | [5 empty] | 0
0
9.4.2 | Underfrequency and Feeder Protection panel - 48U swing frame panel pre-wired to move existing under- | D-DT-5413 | Each | 1 |  |  | 0
| frequency relay to new panel. Panel also to house two (2) x rural feeder protection schemes 4RF1100. | [5 empty] | 0
0
9.4.3 | Remove decommisioned under-frequency panel. Contractor to arrange transport for cables and |  | Sum | 1 |  |  | 0
| panels to nearest Eskom stores. | [5 empty] | 0
0
9.5 | METERING PANEL (TARIFF AND STATISTICAL) | [5 empty] | 0
| Tariff and Statistical metering panel including all accessories as specified as follows: | [5 empty] | 0
9.5.1 | Metering Panel - 48U swing frame panel to house: 1 x Main Tariff meter & 1 x Check Tariff meter per |  | Each | 1 |  |  | 0
| rural feeder ( 2 x feeders). Panel also to house: 1 x Transformer statistical meter. All meters to be class 0,5s, | [5 empty] | 0
| Elster A1700. Panel also to house: Quality-of-Supply module according to Control Plant drawings. | [5 empty] | 0
9.5.2 | Install supervisory cable between the new metering panel and IDF. Also connect existing |  | Sum | 1
RTU to the new cascaded Elster A1700 meters.
9.6 | OTHER EQUIPMENT | [5 empty] | 0
9.6.1 | Install the required MCB module in the existing AC/DC panel as per Control Plant drawings. |  | Each | 1 |  |  | 0
0
9.6.2 | Junction box VRW20 with CT insert | D-DT-5406 | Each | 1 |  |  | 0
0
9.6.3 | Junction Box VRW20 with VT insert | D-DT-5406 | Each | 1 |  |  | 0
0
9.6.4 | Interface Junction Box |  | Each | 1 |  |  | 0
0
9.6.5 | All ancillary equipment/control wiring to interface existing new panels to existing D20 SCADA controller. |  | Each | 1 |  |  | 0
0
9.6.6 | Replace missing 1 x VN95 cell in BTU. |  | Each | 1 |  |  | 0
9.6.7 | MOXA Expansion Kit |  | Each | 1
0
9.7 | FACTORY ACEPTANCE TEST (FAT) | [5 empty] | 0
| Provision for three (3) Engineer and three (3) Employer Representatives and one (1) contractor | [5 empty] | 0
| representatives to witness FAT at manufacturer for the following equipment: | [5 empty] | 0
9.7.1 | 88/22 kV Transformer Protection and Tap Change Panel |  | Sum | 1 |  |  | 0
0
9.7.2 | Underfrequency and Feeder Protection Panel |  | Sum | 1 |  |  | 0
0
9.7.3 | Metering Panel |  | Sum | 1 |  |  | 0
0
9.8 | TESTING AND COMMISSIONING BY OEM ON SITE | [5 empty] | 0
9.8.1 | Transformer Protection and Tap Change panel. Test of protection relays to be done with Omicron Testing | [5 empty] | 0
| Equipment as per Eskom requirements. |  | Sum | 1 |  |  | 0
0
9.8.2 | Underfrequency and Feeder Protection panel. Test of protection relays to be done with Omicron Testing |  | Sum | 1 |  |  | 0
| Equipment as per Eskom requirement. | [5 empty] | 0
0
9.8.3 | Metering Panel |  | Sum | 1 |  |  | 0
0
0
| TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [5 empty] | 0

## LIST J - TRAINING & SPARES
ITEM | DESCRIPTION | REF | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL
10.1 | TRAINING
10.1.1 | Elster A1700 Power Meter - Basic Training Course |  | Each | 4 |  |  | 0
0
10.1.2 | CT Labs Vecto III QoS - Basic Training Course |  | Each | 4 |  |  | 0
0
10.1.3 | ORHVS Training & Registration |  | Each | 4 |  |  | 0
0
10.1.4 | SEL University: APP 101: Hands-On Introduction to SEL Relays |  | Each | 4 |  |  | 0
0
10.1.5 | SEL University: TST 101: SEL Relay Testing Basics |  | Each | 4
10.1.6 | SEL University: TST 103: SEL Feeder Relay Testing |  | Each | 4
10.1.7 | SEL University: PROT 301: Protecting Power Systems for Technicians |  | Each | 4
10.1.8 | SEL University: PROT 300: Symmetrical Components Theory and Application |  | Each | 4
10.1.9 | SEL University: PROT 401: Protecting Power Systems for Engineers |  | Each | 4
10.1.10 | SEL University: PROT 403: Distribution System Protection |  | Each | 4
10.1.11 | SEL University: PROT 411: Substation Equipment Protection |  | Each | 4 |  |  | 0
0
10.1.12 | SEL University: APP 751: SEL-751 Feeder Protection Relay |  | Each | 4 |  |  | 0
0
10.2 | AS BUILT INFORMATION | [5 empty] | 0
| Compile and submit comprehensive As Built manuals and drawings. (Information to be submitted in hard and | [5 empty] | 0
| soft copy). |  | Each | 1 |  |  | 0
0
10.3 | SPARES | [5 empty] | 0
10.3.1 | SEL 751 Directional Relay - Touchscreen |  | Each | 1 |  |  | 0
0
10.3.2 | CT Labs Vecto III portable Quality-of-Supply meter complete with carry-case. |  | Each | 2 |  |  | 0
0
10.3.3 | MOXA rackmount IEC61850 Ethernet switch: PT-7728-R-HV-HV |  | Each | 1 |  |  | 0
0
0
| TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [5 empty] | 0
LV AUXILIARY SUPPLY (Sicelo Substation)
The supply at Sicelo Substation will come from the Midvaal Switchgear Room

## LIST-K MV OH NETWORK
ITEM | DESCRIPTION | REF. | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL:
11.1 | POLE LENGTHS | [5 empty] | 0
| Supply, delivery to pole hole and planting of the following pole sizes: (Poles to be 63 Mpa strength and | [5 empty] | 0
| creosote treated) | [5 empty] | 0
11.1.1 | 9 m wood pole 180-200 mm dia top (Transformer) | 0055 | No | 53 |  |  | 0
0
11.1.2 | 11 m wood pole 180 - 200 mm dia top (MV 1733/1734/1735/1736) | 0051 | No | 145 |  |  | 0
0
11.1.3 | 11 m wood pole 180 - 200 mm dia top (MV 1730) | 0051 | No | 117 |  |  | 0
0
11.1.4 | 12 m wood pole 180 - 200 mm dia top (Provisional) | 0053 | No | 2 |  |  | 0
0
11.1.5 | 2.5 m wooden cross-arm (For transformer drop-out fuses) | 0061 | No | 53 |  |  | 0
0
11.1.6 | 2.5 m wooden cross-arm (Section links) | 0061 | No | 15 |  |  | 0
0
11.2 | MV STRUCTURES/ASSEMBLIES - NOTE INSULATION COORDINATION | [5 empty] | 0
| Supply and dressing of the following MV Structures. | [5 empty] | 0
11.2.1 | Intermediate assembly 0 deg delta 3 ph (600mm steel X-arm D-DT 0335 Sheet 2 ) | 1730 | No | 117 |  |  | 0
0
11.2.2 | Strain assembly vertical 0 deg 3 ph | 1733 | No | 7 |  |  | 0
0
11.2.3 | Strain assembly delta 1 - 60 deg 3 ph | 1734 | No | 81 |  |  | 0
0
11.2.4 | Strain assembly delta 61 - 90 deg 3 ph | 1735 | No | 18 |  |  | 0
0
11.2.5 | Terminal assembly delta 3 phase | 1736 | No | 39 |  |  | 0
0
11.2.6 | Strain assembly H-Pole 1-60 deg 3 ph (provisional) | 1763 | No | 0 |  |  | 0
0
11.2.7 | Section / Equipment links (solid / disconnector assembly) | 1848 | No | 15 |  |  | 0
0
11.2.8 | Delta 3 ph T-off assembly from strain | 1803 | No | 18 |  |  | 0
0
11.2.9 | H-pole transformer structure complete with Transformer platform, bolts, nuts, anti-climb barb wire, warning | [5 empty] | 0
| labels, etc. (Poles, cross arm pole and transformers measured elsewhere). | [5 empty] | 0
| Similar to D-DT1861 - See project drawing | VE9335-7-TRFR | No | 53 |  |  | 0
0
11.2.10 | Complete Transformer "sample" assembly prior to construction | VE9335-7-TRFR | No | 1 |  |  | 0 | 100%
0
11.3 | MV STAYS / STRUTS | [5 empty] | 0
| Supply, dress and tension of the following MV stays / struts | [5 empty] | 0
11.3.1 | Conventional pole stay assembly 380 x 380 plate (2m stay rod) - note insulation co-ordination | 0341 | No | 72 |  |  | 0
0
11.3.2 | Flying stay complete with pole (provisional) | 0343 | No | 1 |  |  | 0
0
11.3.3 | 10m wood strut for 9m pole & assembly (provisional) | 0342 | No | 1 |  |  | 0
0
11.3.4 | 12m wood strut for 11m pole & assembly (including anti-climbing barb wire) | 0351 | No | 65 |  |  | 0
0
11.4 | TRANSFORMERS | [5 empty] | 0
| Supply, installation, connection, testing and commissioning of the following: | [5 empty] | 0
| Transformers as specified with surge arrestors | [5 empty] | 0
11.4.1 | Transformer general arrangement and assembly with all aux. equipment | [5 empty] | 0
| (e.g. insulators, jumpers, S.A.'s etc.) | VE9335-7-TRFR | No | 53 |  |  | 0
0
11.4.2 | 22kV / 420 V - 100 kVA | 3021 | No | 46 |  |  | 0
0
11.4.3 | 22kV / 420 V - 200 kVA | 3021 | No | 7 |  |  | 0
0
11.5 | TRANSFORMER/LOAD BREAKS | [5 empty] | 0
| Supply, installation, connection, testing and commissioning of the following load breaks: | [5 empty] | 0
11.5.1 | Section links cut/out or disconnectors (solid links) | 0293 | Set | 15 |  |  | 0
0
11.5.2 | Drop-out fuses 10 amp assembly with 10 amp fuses (2.5m wooden X-arm measured elsewhere) | 0290 | Set | 46 |  |  | 0
0
11.5.3 | Drop-out fuses 20 amp assembly with 20 amp fuses (2.5m wooden X-arm measured elsewhere) | 0290 | Set | 7 |  |  | 0
0
11.5.4 | LV Fuses Morsdorfers 160A (3 per set) | 3182 | Set | 50 |  |  | 0
0
11.5.5 | LV Fuses Morsdorfers 315A (3 per set) | 3182 | Set | 61 |  |  | 0
0
11.6 | CABLE TERMINATIONS STRUCTURE | [5 empty] | 0
| Supply, installation, connection of the following cable termination structure, complete with surge arrestors, | [5 empty] | 0
| 100 mm dia x 2 500 mm galvanised kicking pipe and galvanised steel kite bracket suitable for cable make off | [5 empty] | 0
11.6.1 | 22 kV, 10 kA surge arrestor for 120 mm2 Al | 0852 | Set | 0 |  |  | 0
0
11.6.2 | 22 kV, 10 kA surge arrestor for 95 mm2 Al | 0852 | Set | 3 |  |  | 0
0
11.7 | EARTHING | [5 empty] | 0
| Supply and install a 3 point star earth for MV network - Consisting of 4 x 1,8 m x 16 mm copper | [5 empty] | 0
| cladded steel earth rod as specified and subject to approval | 0627 | No | 53 |  |  | 0
11.7.1 | Conductive concrete | [5 empty] | 0
| Supply and install conductive concrete per 3 point star on all earth rods (subject to approval) |  | No | 0 |  |  | 0 | 100%
| (provisional) | [5 empty] | 0
0
11.7.2 | Testing earth resistance |  | No | 53 |  |  | 0
0
11.7.3 | Insulation coordination & bonding as per 03TB-34 |  | Sum | 1 |  |  | 0
0
11.8 | CONDUCTORS | [5 empty] | 0
| Supply, stringing and tensioning of the following conductors: | [5 empty] | 0
11.8.1 | FOX (42,8 mm sq ACSR) | 3136 | m | 38200 |  |  | 0
0
11.8.2 | MINK (73.6 mm sq ACSR) | 3136 | m | 0 |  |  | 0
0
11.9 | JOINTS | [5 empty] | 0
| Supply, jointing and tensioning of the following conductors: | [5 empty] | 0
11.9.1 | Full tension line splice for FOX ACSR |  | No | 39 |  |  | 0
0
11.9.2 | Full tension line splice for MINK ACSR (subject to approval) |  | No | 0 |  |  | 0
0
11.10 | EXCAVATION | [5 empty] | 0
| Digging holes, backfilling and compaction to initial soil conditions for poles and anchors | [5 empty] | 0
11.10.1 | Holes for stays/struts 20 x 2 000 | [5 empty] | 0
11.10.1.1 | Earth and soft rock |  | No | 127 |  |  | 0
11.10.1.2 | Hard rock (compressor work) |  | No | 5 |  |  | 0
11.10.1.3 | Hard rock (drilling) |  | No | 5 |  |  | 0
11.10.1.4 | Blasting including over and extra |  | No | 0 |  |  | 0
0
11.10.2 | Hole for 9 m trfr pole | [5 empty] | 0
11.10.2.1 | Earth and soft rock |  | No | 53 |  |  | 0
11.10.2.2 | Hard rock (compressor work) |  | No | 2 |  |  | 0
11.10.2.3 | Hard rock (drilling) |  | No | 2 |  |  | 0
11.10.2.4 | Blasting including over and extra |  | No | 0 |  |  | 0
0
11.10.3 | Hole for 11 m trfr pole | [5 empty] | 0
11.10.3.1 | Earth and soft rock |  | No | 53 |  |  | 0
11.10.3.2 | Hard rock (compressor work) |  | No | 2 |  |  | 0
11.10.3.3 | Hard rock (drilling) |  | No | 2 |  |  | 0
11.10.3.4 | Blasting including over and extra |  | No | 0 |  |  | 0
0
11.10.4 | Hole for 11 m pole | [5 empty] | 0
11.10.4.1 | Earth and soft rock |  | No | 209 |  |  | 0
11.10.4.2 | Hard rock (compressor work) |  | No | 10 |  |  | 0
11.10.4.3 | Hard rock (drilling) |  | No | 10 |  |  | 0
11.10.5 | Blasting including over and extra |  | No | 0 |  |  | 0
11.10.6 | Bags of 50 kg cement added to backfill material as specified on Reticulation layout drawing |  | No | 131 |  |  | 0
11.10.7 | Identify and expose water and sewer services by means off hand cross cut excavations |  | Lot | 1 |  |  | 0
0
11.11 | NUMBERING | [5 empty] | 0
11.11.1 | Provide a pole number - 2 m above ground level with 15 mm punch on 60 mm x 80 mm x 1 mm | [5 empty] | 0
| aluminium plate and fix with 2 x clout nails |  | Lot | 1 |  |  | 0
0
11.11.2 | Transformer Numbering: | [5 empty] | 0
| Number transformers on TRF pole - 2 m above ground level as follows: | [5 empty] | 0
| "TRFR _ " Themba Khubeka and fix with 2 x clout nails: | [5 empty] | 0
| Sheet metal, yellow painted with black letters - 50 mm x 350 mm | [5 empty] | 0
| Letter size to be 28 mm x 15 mm |  | No | 53 |  |  | 0
11.11.3 | Provide an additional pole number label - 2.5m above ground level out of Sheet metal, yellow painted with |  | No | 262
black letters - 50mm x 350mm. Letter size to be 28mm x 15mm.
11.12 | CABLE & AUXILIARY WORK AT SWITCHING STATION | [5 empty] | 0
| Supply, installation and commissioning of the following MV cable. | [5 empty] | 0
11.12.1 | 95 mm², 3 core, Al, 12.7/22 kV PILC, FRPVC SWA |  | m | 83 |  |  | 0
0
11.12.2 | 120 mm², 3 core, Al, 12.7/22 kV PILC, FRPVC SWA |  | m | 0 |  |  | 0
0
11.13 | MV CABLE ENDS | [5 empty] | 0
| Supply, making off and commissioning of cable ends equal or similar to Raytech outdoor type end. | [5 empty] | 0
11.13.1 | 95 mm², 3 core, Al, 12.7/22 kV PILC, FRPVC SWA (indoor) |  | Set | 3 |  |  | 0
0
11.13.2 | 95 mm², 3 core, Al, 12.7/22 kV PILC, FRPVC SWA (outdoor) |  | Set | 3 |  |  | 0
0
11.13.3 | 120 mm², 3 core, Al, 12.7/22 kV PILC, FRPVC SWA (indoor) |  | Set | 0 |  |  | 0
0
11.13.4 | 120 mm², 3 core, Al, 12.7/22 kV PILC, FRPVC SWA (outdoor) |  | Set | 0 |  |  | 0
0
11.14 | CABLE TRENCH | [5 empty] | 0
| Excavation, backfilling and consolidation of cable trenches. | [5 empty] | 0
11.14.1 | Hard rock (compressor) - excavation and backfill |  | m | 0 |  |  | 0
0
11.14.2 | Soft rock and soil - excavation and backfill |  | m | 45 |  |  | 0
0
11.14.3 | Add a concrete slab, 800mm wide x 100mm deep, 250mm above cables in trench to improve cable |  | m | 55 |  |  | 0
| security. (On new feeder cables & existing incomer cables) | [5 empty] | 0
0
11.15 | BEDDING | [5 empty] | 0
| Supply and installation of a 1.2 m.K/W bedding layer per running meter of soft sieved soil in trenches |  | m | 45 |  |  | 0
| as well as backfilling and consolidation as specified. | [5 empty] | 0
0
11.16 | DANGER TAPE | [5 empty] | 0
| Supply and installation of danger tape to a depth of 300 mm. |  | m | 45 |  |  | 0
0
11.17 | CABLE TERMINATION | [5 empty] | 0
11.17.1 | Supply and install a cable termination bracket including surge arrestors and auxiliaries | D-DT-0851 | Each | 3 |  |  | 0
0
11.17.2 | Improve cable termination security - fill galvanised kicking pipe with concrete. |  | Each | 3 |  |  | 0
0
11.18 | CABLE TESTING | [5 empty] | 0
| Perform the following tests and supply certificates: | [5 empty] | 0
11.18.1 | Factory testing of cables with certificates |  | Sum | 1 |  |  | 0
0
11.18.2 | Bedding test certificates (three tests) |  | Sum | 1 |  |  | 0
0
11.18.3 | Commissioning test certificates |  | Sum | 1 |  |  | 0
0
TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [6 empty] | 0

## LIST-L LV NETWORK
ITEM | DESCRIPTION | REF. | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | CONTRACT TOTAL:
12.1 | POLE LENGTHS | [5 empty] | 0
| Supply and install the following 63 MPa, creosote treated wood poles | [5 empty] | 0
12.1.1 | 7 m wooden pole 120 - 139 mm dia top (kicker pole) | 0050 | No | 51 |  |  | 0
0
12.1.2 | 9 m wooden pole 160 - 179 mm dia top | 0055 | No | 818 |  |  | 0
0
12.2 | LV STRUCTURES | [5 empty] | 0
12.2.1 | Intermediate/Suspension (0 - 30 deg) | 1100 | No | 520 |  |  | 0
0
12.2.2 | Strain assembly (0 - 60 deg) | 1121 | No | 50 |  |  | 0
0
12.2.3 | Strain assembly (60 - 90 deg) | 1122 | No | 89 |  |  | 0
0
12.2.4 | Terminal assembly | 1120 | No | 300 |  |  | 0
0
12.2.5 | T-off assembly from intermediate | 1140 | No | 58 |  |  | 0
0
12.2.6 | T-off assembly from strain | 1142 | No | 19 |  |  | 0
0
12.2.7 | Cross intermediate-intermediate assembly | 1141 | No | 9 |  |  | 0
0
12.2.8 | Cross intermediate-strain assembly | 1143 | No | 1 |  |  | 0
0
12.2.9 | Complete pole top box and house connection "sample" assembly prior to construction |  | Lot | 1 |  |  | 0
0
12.3 | L V ANCHORS | [5 empty] | 0
| Supply, dress and tension the following LV stays / struts | [5 empty] | 0
12.3.1 | Conventional pole stay assembly (300 x 300 plate & 1.5m stay rod) | 0341 | No | 405 |  |  | 0
0
12.3.2 | Flying stay complete with pole (provisional) | 0343 | No | 1 |  |  | 0
0
12.3.3 | 10 m wood strut for 9 m pole | 0351 | No | 63 |  |  | 0
0
12.4 | SERVICE CONNECTION BOXES | [5 empty] | 0
| Supply and install Pole Mounted Split Meter Box: | [5 empty] | 0
12.4.1 | 1-2 way service dist pole top box (VE9335-7-PTB) (Allbro Alltilt) | 3055 | No | 227 |  |  | 0
0
12.4.2 | 1-4 way service dist pole top box (VE9335-7-PTB) (Allbro Alltilt) | 3055 | No | 452 |  |  | 0
0
12.4.3 | 1-6 way service dist pole top box (VE9335-7-PTB) (Allbro Alltilt) | 3055 | No | 28 |  |  | 0
0
12.4.4 | 40 A MCB, slow curve 1, 5 kA |  | No | 2361 |  |  | 0
0
12.4.5 | LV lightning arrestor, Hy-mag clip in type SAL |  | No | 2361 |  |  | 0
0
12.5 | EXTRA EARTHING | [5 empty] | 0
12.5.1 | Supply and install a 3 point star earth for LV network - Consisting of 4 x 1,8 m x 16 mm copper | [5 empty] | 0
| earth rod as specified and subject to approval | 0637 | No | 111 |  |  | 0
0
12.5.2 | Conductive concrete | [5 empty] | 0
| Supply and install conductive concrete per 3 point star on all earth rods (subject to approval) |  | No | 0 |  |  | 0
0
12.5.3 | Testing earth resistance |  | No | 111 |  |  | 0
0
12.6 | STRINGING | [5 empty] | 0
| Supply and stringing of the following aerial bundle conductor (ABC) | [5 empty] | 0
0
12.6.1 | 3 x 35 mm sq aerial bundle conductor + bare neutral conductor | 3141 | m | 10150 |  |  | 0
0
12.6.2 | 3 x 70 mm sq aerial bundle conductor + bare neutral conductor | 3141 | m | 14100 |  |  | 0
0
12.7 | JOINTS (Subject to Approval) | [5 empty] | 0
0
12.7.1 | 35 mm sq ABC (4 core) |  | No |  |  |  | 0
0
12.7.2 | 70 mm sq ABC (4 core) |  | No |  |  |  | 0
0
12.8 | POLE NUMBERING | [5 empty] | 0
| Numbering of LV poles |  | No | 869 |  |  | 0
0
12.9 | EXCAVATION OF POLE HOLES | [5 empty] | 0
| Holes for stays and struts (12 x 1500 rod) | [5 empty] | 0
12.9.1 | Ground and soft rock |  | No | 386 |  |  | 0
0
12.9.2 | Hard rock (compressor) |  | No | 10 |  |  | 0
0
12.9.3 | Hard rock (drilling) |  | No | 10 |  |  | 0
0
12.9.4 | Blasting including over and extra |  | No | 0 |  |  | 0
0
| Hole for 7 m pole | [5 empty] | 0
12.9.5 | Ground and soft rock |  | No | 47 |  |  | 0
0
12.9.6 | Hard rock (compressor) |  | No | 2 |  |  | 0
0
12.9.7 | Hard rock (drilling) |  | No | 2 |  |  | 0
0
12.9.8 | Blasting including over and extra |  | No | 0 |  |  | 0
0
| Hole for 9 m pole | [5 empty] | 0
12.9.9 | Ground and soft rock |  | No | 738 |  |  | 0
0
12.9.10 | Hard rock (Compressor) |  | No | 40 |  |  | 0
0
12.9.11 | Hard rock (Drilling) |  | No | 40 |  |  | 0
0
12.9.12 | Blasting including over and extra |  | No | 0 |  |  | 0
0
12.9.13 | Bags of 50 kg cement added to backfilling |  | No | 435 |  |  | 0
0
12.9.14 | Identify and expose sewer and water services by means of hand cross cut excavations |  | Sum | 1 |  |  | 0
0
12.10 | TESTING AND COMMISSIONING OF LV NETWORK PER TRANSFORMER AREA |  | No | 53 |  |  | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [6 empty] | 0

## LIST-M HOUSE CONNECTIONS
ITEM | DESCRIPTION | REF. | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | CONTRACT TOTAL:
13.1 | HOUSE CONNECTIONS | [5 empty] | 0
13.1.2 | Supply, delivery, installation and commissioning of ready boards complete with light-fitting and lamp as | [5 empty] | 0
| specified. One socket outlet to comply with the requirements of SANS 164-2. Includes backboard or | 0360 | No | 2361 |  |  | 0
| mounting rails. | [5 empty] | 0
0
13.1.3 | Supply, delivery, installation and connecting of drip looped 10 mm² split concentric SNE Airdac house | [5 empty] | 0
| connection cable as specified (SNE Separate Neutral Earth) | 3140 | m | 54300
0
13.1.4 | Supply, install, connecting and testing of Conlog split single phase pre-payment meter complete with interface | [5 empty] | 0
| and Din Rail Mounted Power Line Carrier Meter | 3145 |  |  |  |  | 0
13.1.4.1 | DIN Rail RF Meter Control Unit (Conlog or Similar - to comply/correspond with existing installation) |  | No | 2361 |  |  | 0
0
13.1.4.2 | DIN Rail RF User Interface Unit (Conlog or Similar - to comply/correspond with existing installation) |  | No | 2361 |  |  | 0
0
13.1.4.3 | EA VARISTOR PDZ32 440CW 5kA 40V Metal Oxide. |  | No | 2361 |  |  | 0
0
13.1.4.4 | Suitable Cable Gland, Nylon, with Lock Nut, for SNE Airdac. |  | No | 2361 |  |  | 0
0
13.1.4.5 | Supply and installation of weather proof type York wall mounted box with wooden backing plate to | [5 empty] | 0
| accommodate prepaid meter on outer side of house |  | No | 0 |  |  | 0
0
13.1.4.6 | Supply and installation of Airdac strain clamps complete for fixing at pole and house with pigtail hook or | [5 empty] | 0
| bracket suitable for both wooden truss or wall mounting | 0360 | No | 2361 |  |  | 0
0
13.1.4.7 | Supply and install pigtail bolt assembly (M10 x 280 mm) |  | No | 2361 |  |  | 0
0
13.1.4.8 | Supply and installation of 5 m wooden shack pole complete with excavation, subject to approval | 0058 | No | 2361 |  |  | 0
| (provisional) | [5 empty] | 0
0
13.1.4.9 | Testing and quality control (ID number, Co-ordinates, etc.) of house connection installation and issuing of a | [5 empty] | 0
| certificate of compliance for each house connection by an accredited person as specified. |  | No | 2361 |  |  | 0
0
13.1.4.10 | Issue a CoC for each installation. |  | No | 2361 |  |  | 0
0
13.2 | LOCAL SUB-CONTRACTORS | [5 empty] | 0
13.2.1 | Allow R300,00 / house connection for labour of local subcontractors. |  | No | 2361 |  |  | 0
0
13.2.2 | Tools, Training, PPE & Management of local sub-contractors |  | Sum | 1 |  |  | 0
| Note: Local sub-contractors to be appointed as employees of the main contractor for task related services | [5 empty] | 0
| (Main Contractor liability insurance shall cover the sub-contractor) | [5 empty] | 0
TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [6 empty] | 0

## LIST-N MV SW-GR & CNTR (Themba)
ITEM | DESCRIPTION | REF. | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL
14.1 | 22 kV SWITCHGEAR & CONTROL GEAR | [5 empty] | 0
| Supply, installation and commissioning by OEM of metal clad switchgear equal or similar to Alstom type | VE9335-7-SGS |  |  |  |  | 0
| 1250 A SBV24L, vacuum switchgear as specified and as shown on drawings. A single busbar system, rated | [5 empty] | 0
| 25 kA. An aluminium ladder to be provided to access all equipment. | [5 empty] | 0
14.1.1 | Feeder panels, 800 A | VE9335-7-SGS | Each | 3 |  |  | 0
0
14.1.2 | Protection IED (local on switchgear) - RING FEEDER (O/C E/F) | VE9335-7-SGS | Each | 3
14.1.3 | Chauvin Arnoux Enerium Enerdis-50 type Measuring centres | VE9335-7-SGS | Each | 3 |  |  | 0
0
14.1.4 | Protection IED software licensing (fault analysis) |  | Sum | 1 |  |  | 0
0
14.1.5 | MV Control plant section of the SCADA system c/w terminations, glanding, schemes, programming and all | [5 empty] | 0
| related auxiliaries |  | Sum | 1 |  |  | 0
14.1.6 | Supply and install 50x50x6MM angle iron bolted to concrete to traverse across trench for switchgear | VE9335-7-SGS | Each | 6
support and mounting.
0
14.2 | EARTHING OF MV SWITCHGEAR | [5 empty] | 0
14.2.1 | 250 mm2 Earth bar, connection of switchgear earth bar to existing trench earth bar. |  | Sum | 1 |  |  | 0
0
14.2.2 | Earthing of CB racking plates and connection of surface bed reinforcing to earth. |  | Sum | 1 |  |  | 0
0
14.3 | COMMISSIONING & TESTING | [5 empty] | 0
| Provision for two (2) Engineer representatives and two (2) Employer representatives and one (1) contractor | [5 empty] | 0
| representatives to witness FAT at manufacturer as specified for the following equipment: | [5 empty] | 0
14.3.1 | 22 kV Switchgear Panels [including metering (energy) at the manufacturers works] |  | Sum | 1 |  |  | 0
0
14.3.2 | SAT Commissioning of Switchgear Panels |  | Sum | 1 |  |  | 0
14.3.3 | Commision existing SCADA system connected with the new feeder panels |  | Sum | 1 |  |  | 0
0
14.3.4 | Site protection re-commissioning, setting & testing by Lyon and Partners |  | PC | 1 | 15000 |  | 15000
0
14.4 | SCADA | [5 empty] | 0
14.4.1 | Implement the necessary communication wiring to control the new feeder panels via the existing local SCADA |  | Each | 1 |  |  | 0
| system. | [5 empty] | 0
14.4.2 | Add the new feeder panels to the existing HMI (panels should be able to be remotely operated from the HMI). |  | Each | 1 |  |  | 0
0
14.4.3 | Supply and install the necessary Email software package for the existing Orion LXm RTU so that an email is |  | Each | 1 |  |  | 0
automatically sent when there is an alarm on the HMI.
0
14.4.4 | Supply and setup a desktop and 24inch screen for Metsimaholo LM's workshop. Desktop to be set up as a | [5 empty] | 0
| "Viewer" for the HMI. Desktop computer with 8GB RAM, 256GB SATA SSD, 1TB HDD. |  | Sum | 1
0
14.4.5 | All cabling & other auxiliaries |  | Sum | 1 |  |  | 0
0
14.5 | COMMUNICATION & CONTROL CABLING C/W ALL AUXILIARIES | [5 empty] | 0
14.5.1 | Any wiring requirements not catered for elsewhere i.e. between switchgear and SCADA control panel |  | Sum | 1 |  |  | 0
0
14.6 | TELEMETRY | [5 empty] | 0
| Supply and install the necessary gateway/repeater/communication hardware at Metsimaholo LM's workshop to | [5 empty] | 0
| interface the desktop mentioned above with the SCADA system. Take note of the as-built information | [5 empty] | 0
| regarding the SCADA systems communication link between the Themba Khubeka S/S, Metsimaholo LM's workshop and Metsimaholo LM. | [5 empty] | 0
14.6.1 | Configuration |  | Sum | 1 |  |  | 0
0
14.6.2 | Testing and Commissioning |  | Sum | 1 |  |  | 0
0
14.6.3 | Training of the customers personnel |  | Sum | 0 |  |  | 0
0
14.6.4 | Telemetry Equipment required for integration at Metsimaholo LM's workshop so that the HMI can be viewed | [5 empty] | 0
| on the desktop and screen that is to be supplied under "SCADA" (gateways/RTU/switch etc. that may be |  | Sum | 1 |  |  | 0
| required) | [5 empty] | 0
0
14.6.5 | Allow communication to the HikVision NVR over internet connection to allow mobile devices (cellphones) |  | Sum | 1 |  |  | 0
to access the existing HikVision NVR.
0
TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [6 empty] | 15000

## LIST-O Substation Rep & Comm.
ITEM | DESCRIPTION | REF. | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL
15.1 | MUNICIPAL SUBSTATION REPAIR | [5 empty] | 0
15.1.1 | Service of 88kV Isolators |  | Ea | 9 |  |  | 0
0
15.1.2 | Service of 88kV Circuit Breakers |  | Ea | 4 |  |  | 0
0
15.1.3 | 88/11kV Transformer Oil Test and Servicing |  | Ea | 1 |  |  | 0
15.1.4 | Service of 11kV NECRT |  | Ea | 2
0
15.1.5 | 630mm² x 1Core, 6.35/11kV, XLPE cable |  | m | 420 |  |  | 0
0
15.1.6 | 630mm² x 1Core XLPE: Indoor Cable End |  | Ea | 12 |  |  | 0
0
15.1.7 | 630mm² x 1 Core XLPE: Outdoor Cable End |  | Ea | 12 |  |  | 0
15.1.8 | Replace/Repair ABB RED670 Relay |  | Ea | 1
15.1.9 | Commission "Feeder No 2" Switchgear Panel |  | Ea | 1 |  |  | 0
0
15.1.10 | Repair and re-commissioning of SCADA system |  | Ea | 1 |  |  | 0
0
15.1.11 | Service 88kV BTUs |  | Ea | 1 |  |  | 0
0
15.1.12 | Service 11kV BTUs |  | Ea | 1 |  |  | 0
0
15.1.13 | Remove weeds and apply herbicides. |  | Ea | 1 |  |  | 0
0
15.1.14 | Repair/Re-instate alarm system |  | Ea | 1 |  |  | 0
0
15.1.15 | Repair Burglar Proofing |  | Sum | 1
|  |  | Sum | 1 |  |  | 0
0
TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES | [6 empty] | 0

## LIST-P Overhead Line Repair
ITEM | DESCRIPTION | REF. | UNIT | QTY | UNIT LABOUR RATE | UNIT MATERIAL RATE | TOTAL
16.1 | OHL REPAIR
16.1.1 | Preliminary & General Cost (Fixed & Time Related) |  | Sum | 1 |  |  |  | Sum | 1 | 0
16.1.2 | Survey of OHL |  | Sum | 1
16.1.3 | Palm Compression Clamps |  | Ea | 6
16.1.4 | Recompaction of Stay Excavations |  | Ea | 170
16.1.5 | OPGW Trench Excavation Compaction |  | m | 300
16.1.6 | Line Terminal Connection to Substation Earth Grid |  | Ea | 4
0
16.1.7 | Clear all structure bases |  | Ea | 47 | [5 empty] | 0
16.1.8 | Apply Bitumen paint to pole bases |  | Ea | 47
16.1.9 | Bush clearing and removal of 1 x streetlight |  | Sum | 1
16.1.10 | Implement and test Earth/Footing resistance at each pole |  | Ea | 47
16.1.11 | Tension Charts/ Construction Handbook |  | Sum | 1
16.1.12 | Retension double-circuit spans, circuit with lower tension to be tensioned equal to other circuit. |  | Ea | 12
16.1.13 | Tying down of stay wire |  | Ea | 170
16.1.14 | Retensioning of all stays and tying stay wire down |  | Ea | 170
16.1.15 | Check circuit tension on all strain poles |  | Sum | 1
16.1.16 | Confirmation that the Shield Wire bracket is designed for 2 x shield wires |  | Sum | 1
16.1.17 | Provide burn-off time of shield wire and OPGW in parallel. |  | Sum | 1
16.1.18 | Relabel all pole labels |  | Ea | 70
16.1.19 | Provide line crossing labels |  | Ea | 12
16.1.20 | Shield wire insulated assembly |  | Ea | 4
16.1.21 | Provide phasing discs |  | Ea | 6
16.1.22 | Implement/Confirm phase swap. |  | Sum | 1
16.2 | PHASE CONDUCTOR CLOSING SPAN TO MUNICIPAL SUBSTATION
16.2.1 | Conductor |  | m | 200
16.2.2 | Hardware |  | Span | 6
16.3 | X-BRACED STRAIN STRUCTURE TO BE REPLACED
16.3.1 | Removal of existing structure |  | Sum | 1
16.3.2 | New free-standing monopole structures |  | Ea | 2
16.3.3 | Monopole structure foundation |  | Ea | 2
16.3.4 | String from new structure to other structures (3 Phases & Shield Wire & OPGW) |  | m | 1450
16.3.5 | Provide OEM labels for all poles |  | Sum | 1
16.4 | TERMINATE OPGW AT ESKOM SUBSTATION
16.4.1 | Fibre Testing (12F) |  | Sum | 1
16.4.2 | Dismantle Current ADSS |  | m | 490
16.4.3 | Restring ADSS |  | m | 480
16.4.4 | Hardware |  | Sum | 1
TOTAL CARRIED FORWARD TO SUMMARY OF BILL OF QUANTITIES